## ESTIMATE
AMOUNT
|  | PROJECT: | CITY OF LYTLE, REMOTE WATER WELL NO. 5 (CSB#2026-08-02), incl. Addendum No. 1 (8/20/2026) |  |  | Subtotal |  |  |  |  | 1880600.3405
[6 empty] | Over & Profit |  |  |  |  | 940300.1702
|  | LOCATION: | 14865 W FM 2790 S, Lytle (Medina County), TX 78052
[6 empty] | Total |  |  |  |  | 2820900.5107
S# | Dwg. | BID ITEM | DESCRIPTION | QTY. | Wastage | Qty w/ Waste | UNIT | UNIT LABOR COST | UNIT MATERIAL COST | TOTAL LABOR COST | TOTAL MATERIAL COST | TOTAL COST
|  | 1 | BID ITEM 1: MOBILIZATION & GENERAL CONDITIONS
MOBILIZATION
1 | Spec 01502 | 1 | Mobilization / demobilization of all trades, well drilling rig, service rig & crane (bid form cap: max 5% of Total Base Bid) | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
PROJECT MANAGEMENT & SUPERVISION
2 | Spec 01010, 01270 | 1 | Project management, coordination with City, Engineer (Cobb Fendley), Well No. 4 operator & utilities (AEP/POCO, gas co.) | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
3 | Spec 01010; Sp. Cond. III | 1 | Full-time superintendent / site supervision (max 250 calendar days to substantial completion per Bid Form) | 9 | 0% | 9 | MO | 0 | 0 | 0 | 0 | 0
4 | Spec 01010; Sp. Cond. III | 1 | Construction schedule, progress meetings & monthly pay applications | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
SURVEY & LAYOUT
5 | Sp. Cond. II; Bid Form (k) | 1 | Construction staking & layout by licensed surveyor (site, building, fence, 1,080 LF collection line, well location Lat 29°16'42.55" / Long 98°48'19.55") | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
SUBMITTALS
6 | Spec 01330, 01340 | 1 | Submittals, shop drawings, product data & samples (incl. well materials, pump curves, chlorination 5 sets per WP-240 §8.01) | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
PERMITS
7 | Sh 2 Gen Note 3; Spec 13200 §1.03-H | 1 | Permits: Medina County ROW/culvert & floodplain, TxDOT 72-hr notice, TDLR/TCEQ well filings, EAA well construction coordination, mud/fluids disposal permits | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
TESTING & SPECIAL INSPECTIONS
8 | Sh 3 Str Gen Info 6-7; Spec 01450, 01454 | 1 | Construction materials testing by contractor-furnished lab (concrete cylinders, compaction/proctors, masonry unit & grout per Sh 3 CMU Note 10) | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
9 | Sh 3 Gen Str Note 10; Spec 01452 | 1 | Special inspection coordination (rebar placement, concrete pours, post-installed anchors, masonry per TMS 402 Tbl 1.18.3) | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
TEMPORARY FACILITIES
10 | Spec 01504 | 1 | Field office / storage container on 40' x 60' contractor laydown area (Sh 5) | 9 | 0% | 9 | MO | 0 | 0 | 0 | 0 | 0
11 | Sh 2 TCEQ Note 5; Spec 13200 §2.02-D | 1 | Temporary toilet, sealed, leak-proof type only (none within 150 ft of well unless sealed type) | 9 | 0% | 9 | MO | 0 | 0 | 0 | 0 | 0
12 | Spec 01504; Addendum 1 Clar. 1 | 1 | Temporary power & construction lighting (all lights aimed away from nearby residents per Addendum 1) | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
TEMPORARY CONTROLS (SECURITY, TRAFFIC & DUST)
13 | Sh 2 Gen Note 10; Spec 01504 | 1 | Temporary site security fencing / barricades during darkness & periods of inactivity | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
14 | Spec 01555; Sh 2 Gen Note 13 | 1 | Traffic control at CR 5714 driveway & FM 2790 frontage per TxMUTCD Part VI (signs, flagger during deliveries/rig moves) | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
15 | Spec 01504 | 1 | Dust control & daily site cleanup | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
CLOSEOUT & WARRANTY
16 | Spec 01770, 01785 | 1 | Project record (as-built) drawings, well records & closeout documents | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
17 | Spec 13200 §1.04-C; WP-240 §11.01 | 1 | Operation & maintenance manuals (3 copies well/pump; 4 copies chlorination) | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
18 | Spec 01770; 13200 §3.30 | 1 | Final cleaning, punch list & one-year warranty administration | 1 | 0% | 1 | LS | 0 | 0 | 0 | 0 | 0
|  |  | Subtotal | [6 empty] | 0 | 0 | 0
|  | 2 | BID ITEM 2: SWPPP IN ACCORDANCE WITH TPDES REQUIREMENTS
SWPPP DOCUMENTATION, INSPECTION & MAINTENANCE
19 | Spec 01570 | 2 | SWP3 preparation, TPDES CGP (TXR150000) Notice of Intent (NOI), site notice & Notice of Termination (NOT) | 1 | 0% | 1 | LS | 3500 | 250 | 3500 | 250 | 3750
20 | Spec 01570 | 2 | SWPPP inspections, reporting & BMP maintenance throughout project duration | 9 | 0% | 9 | MO | 650 | 50 | 5850 | 450 | 6300
SILT FENCE, INLET PROTECTION & ROCK FILTER DAMS
21 | Sh 8 (extent of grading); Spec 01570 | 2 | Reinforced filter fabric barrier (silt fence), downslope perimeter of well-site grading limits & collection line corridor | 928.6 | 5% | 975.03 | LF | 1.35 | 1 | 1316.2905 | 975.03 | 2291.3205
22 | Sh 8 & 19; Spec 01570 | 2 | Inlet protection barrier at 12" CMP culvert inlet/outlet (CR 5714 roadside ditch) | 2 | 0% | 2 | EA | 150 | 125 | 300 | 250 | 550
23 | Sh 8; Spec 01570 | 2 | Rock filter dam, roadside ditch downstream of site (match existing ditch flowline) | 2 | 0% | 2 | EA | 650 | 750 | 1300 | 1500 | 2800
STABILIZED CONSTRUCTION ACCESS & WASHOUT
24 | Sh 5; Spec 01575 | 2 | Stabilized construction access at CR 5714 drive (approx. 20' x 50', rock over geotextile) incl. maintenance | 1 | 0% | 1 | EA | 1500 | 2200 | 1500 | 2200 | 3700
25 | Spec 01570 | 2 | Concrete truck washout pit (lined) | 1 | 0% | 1 | EA | 450 | 400 | 450 | 400 | 850
BMP REMOVAL
26 | Spec 01570; 13200 §1.02-C/D; Addendum 1 Clar. 4 | 2 | Removal of temporary BMPs at final stabilization | 1 | 0% | 1 | LS | 1500 | 0 | 1500 | 0 | 1500
|  |  | Subtotal | [6 empty] | 15716.2905 | 6025.03 | 21741.3205
|  | 3 | BID ITEM 3: CHAIN LINK FENCE WITH 16-FOOT & 10-FOOT SWING GATES
FENCE LINE (FABRIC, POSTS, FOOTINGS & SLATS)
27 | Sh 5, 18; Spec 02821 | 3 | 6'-0" galv. chain link fence, 2" x 9 ga mesh, 3-strand 12-1/2 ga barbed wire (1'-0" ext.), 1-5/8" top rail, 7 ga tension wire, well site 80'x60' | 409 | 0% | 409 | LF | 7.5 | 9.5 | 3067.5 | 3885.5 | 6953
28 | Sh 18 (Site Perimeter Chain Link Fencing) | 3 | 2-3/8" OD line posts @ 10'-0" max in 9" dia x 3'-0" Class "CB" concrete footings, domed | 40.9 | 0% | 40.9 | EA | 55 | 60 | 2249.5 | 2454 | 4703.5
29 | Sh 18 | 3 | 2-7/8" OD terminal / corner / pull posts with 1-5/8" braces & 3/8" truss rods, 12" dia concrete footings | 8 | 0% | 8 | EA | 125 | 175 | 1000 | 1400 | 2400
30 | Spec 02821 §2.01-J | 3 | 1-1/8" dark green PVC privacy slats, entire fence except gates (6' ht) | 2304 | 5% |  | SF | 1.25 | 2.1 | 0 | 0 | 0
16' VEHICLE GATE & 10' SWING GATE
31 | Sh 18 (Typical Double Vehicle Gate) | 3 | 4" Sch 40 gate posts in 18" dia concrete footings | 4 | 0% | 4 | EA | 185 | 265 | 740 | 1060 | 1800
32 | Sh 5, 18 | 3 | 16'-0" double swing vehicle gate (2 leaves), 1.90" OD frame, 180° hinges, drop rod, center stop, latch & padlock (3 keys) | 1 | 0% | 1 | EA | 450 | 1650 | 450 | 1650 | 2100
33 | Sh 5, 18 (Security Fence and Gate) | 3 | 10'-0" swing gate at electrical service area, 1.90" OD frame, Type 71 latch & padlock (3 keys) | 1 | 0% | 1 | EA | 300 | 1050 | 300 | 1050 | 1350
SIGNAGE
34 | Sh 18 (14"x10" Typical Danger Signage); Sh 2 TCEQ Note 14 | 3 | 14"x10" "DANGER - CHLORINE" and "DANGER - HIGH VOLTAGE" signs & site ID signage on fence/gates per City & TCEQ | 4 | 0% | 4 | EA | 35 | 65 | 140 | 260 | 400
|  |  | Subtotal | [6 empty] | 7947 | 11759.5 | 19706.5
|  | 5 | BID ITEM 5: 12-INCH WATER LINE (WELL COLLECTION LINE) (1,080 LF)
12" C900 PIPE INSTALLATION (TRENCH, BEDDING, PIPE & BACKFILL)
35 | Sh 17 (Bedding & Backfill); Spec 02317, 02320 | 5 | Trench excavation, 4' min. cover (Sh 2 Water Note 11), approx. 2.5' W x 5.6' D | 560 | 0% | 560 | CY | 6.5 | 4.5 | 3640 | 2520 | 6160
36 | Sh 17; Spec 02320 | 5 | Pipe embedment / bedding material (6" below to 12" above pipe) | 222 | 10% | 244.2 | CY | 12 | 32 | 2930.4 | 7814.4 | 10744.8
37 | Sh 4, 5; Sh 2 Water Note 2; Spec 02506 | 5 | 12" AWWA C900 DR-18 PVC (blue) pressure pipe, push-on joints, Well 5 to Well 4 | 1080 | 2% | 1101.6 | LF | 9 | 38 | 9914.4 | 41860.8 | 51775.2
38 | Sh 17; Spec 02317 | 5 | Trench backfill with select native, compacted in lifts | 300 | 0% | 300 | CY | 6 | 4 | 1800 | 1200 | 3000
39 | Sh 2 Gen Note 11; Spec 02260 | 5 | Trench safety system (OSHA 29 CFR 1926 Subpart P) for trenches ≥5' deep | 1080 | 0% | 1080 | LF | 1.5 | 1.5 | 1620 | 1620 | 3240
40 | Standard practice (not detailed) | 5 | #12 AWG tracer wire & detectable warning tape over PVC line | 1080 | 5% | 1134 | LF | 0.45 | 0.6 | 510.3 | 680.4 | 1190.7
FITTINGS & THRUST RESTRAINT
41 | Sh 5 ((2) 12" 45° bends, M.J.); Spec 02501 | 5 | 12" x 45° DI compact bends, MJ, cement-mortar lined (ANSI A21.53, 250 psi) with MJ restraint glands | 6 | 0% | 6 | EA | 225 | 650 | 1350 | 3900 | 5250
42 | Sh 17 (Thrust Block Detail 4"-12") | 5 | Concrete thrust blocks at 12" 45° bends (Class B, against undisturbed soil) | 6 | 0% | 6 | EA | 185 | 165 | 1110 | 990 | 2100
43 | Sh 9 (Item 13/15) to PVC transition | 5 | 12" DI flange x MJ / PVC transition adapter at well header discharge | 1 | 0% | 1 | EA | 250 | 750 | 250 | 750 | 1000
TESTING & DISINFECTION
44 | Sh 2 Water Note 10; Spec 02515 | 5 | Hydrostatic testing of 12" collection line (entire footage) | 1080 | 0% | 1080 | LF | 0.85 | 0.15 | 918 | 162 | 1080
45 | Sh 2 Water Note 7, Hyper-Chlor Notes; Spec 02514 | 5 | Disinfection (AWWA C651), flushing & dechlorination (AWWA C655) incl. bacteriological samples (1 per 1,000 LF = 2 min.) | 1080 | 0% | 1080 | LF | 0.95 | 0.35 | 1026 | 378 | 1404
EXISTING UTILITY CROSSINGS
46 | Sh 4 & 7 (exist. gravel drive, 3" gas line, overhead elec.) | 5 | Crossings / protection of existing utilities & gravel drive along route; potholing at points of crossing (Sh 2 Gen Note 4) | 1 | 0% | 1 | LS | 3500 | 1500 | 3500 | 1500 | 5000
|  |  | Subtotal | [6 empty] | 28569.1 | 63375.6 | 91944.7
|  | 6 | BID ITEM 6: SITE RESTORATION, HYDRO-MULCH SEEDING & REGRADING
CLEARING & GRUBBING
47 | Sh 8 (extent of proposed grading); Spec 02201 | 6 | Clearing, grubbing & stripping (tilled agricultural field) within limits of grading at Well 5 site | 1.7 | 0% | 1.7 | AC | 1100 | 650 | 1870 | 1105 | 2975
48 | Sh 4 & 7; Spec 02201 | 6 | Clearing & grubbing along 12" collection line corridor (±1,080 LF x 20' construction width) | 0.5 | 0% | 0.5 | AC | 1500 | 800 | 750 | 400 | 1150
GRADING & FILL
49 | Sh 8; Sh 2 Grading Notes; Spec 02201 | 6 | Rough & fine grading to finished grades (FG 769.10 to 771.25), -5.0% from high point to EG, positive drainage; well head -2% min for 5'-0" (Sh 8 Note 1) | 80670.1 | 0% | 80670.1 | SF | 0.14 | 0.1 | 11293.814 | 8067.01 | 19360.824
50 | Sh 8; Spec 02201 | 6 | Embankment / import fill to raise well pad & building area to FG 771.00 (cut/fill not balanced on plans, verify with topo) | 450 | 15% | 517.5 | CY | 9 | 22 | 4657.5 | 11385 | 16042.5
SEEDING & ESTABLISHMENT
51 | Spec 01740, 02921 | 6 | Hydro-mulch seeding (Bermuda/Rye per season), fertilizer 10-20-10, mulch & tackifier, all disturbed areas at Well 5 site | 7100 | 0% | 7100 | SY | 0.55 | 0.6 | 3905 | 4260 | 8165
52 | Spec 01740, 02921 | 6 | Hydro-mulch seeding, 12" collection line corridor & Well No. 4 disturbed areas | 2400 | 0% | 2400 | SY | 0.55 | 0.6 | 1320 | 1440 | 2760
53 | Spec 02921 | 6 | Vegetative watering until establishment (90% coverage) | 1 | 0% | 1 | LS | 3500 | 1500 | 3500 | 1500 | 5000
RESTORATION OF EXISTING FEATURES
54 | Sh 2 Gen Note 8; Spec 01740 | 6 | Restoration of existing ditches, drives, fences & ROW disturbed by construction to existing or better condition | 1 | 0% | 1 | LS | 3500 | 2000 | 3500 | 2000 | 5500
|  |  | Subtotal | [6 empty] | 30796.314 | 30157.01 | 60953.324
|  | 7 | BID ITEM 7: CHLORINE DISINFECTION IN BUILDING (WP-240)
CHLORINATORS & VACUUM REGULATORS
55 | WP-240 §2.01-A; Sh 12 Rev. (CL-1, CL-2) | 7 | W&T Series S10K remote vacuum chlorinators, 50 PPD rotameters & injector throats, manual rate / auto start-stop, 5 mg/L, 10:1 turndown (CL-1 duty + CL-2 backup) | 2 | 0% | 2 | EA | 650 | 6200 | 1300 | 12400 | 13700
56 | WP-240 §2.01-B | 7 | W&T Model 200C container-mounted vacuum regulator check units w/ automatic switchover & G1123 filter trap assemblies | 2 | 0% | 2 | EA | 350 | 3800 | 700 | 7600 | 8300
57 | WP-240 §2.01-A | 7 | Spare 100 PPD rotameter & injector throat assembly | 1 | 0% | 1 | EA | 0 | 950 | 0 | 950 | 950
58 | WP-240 §2.01-A | 7 | Complete spare parts kit per chlorinator | 2 | 0% | 2 | EA | 0 | 850 | 0 | 1700 | 1700
CYLINDERS, RESTRAINTS & SCALES
59 | Sh 12 Rev. ((4) 150 lb cylinders + extra cylinders chained to walls) | 7 | 150-lb chlorine gas cylinders, initial supply (4 in service + 3 spare shown; confirm whether Owner-furnished) | 7 | 0% | 7 | EA | 25 | 550 | 175 | 3850 | 4025
60 | WP-240 §2.01 | 7 | 316 SS safety chains & wall brackets for in-service & auxiliary cylinders | 7 | 0% | 7 | SET | 65 | 145 | 455 | 1015 | 1470
61 | WP-240 §2.01-D | 7 | Flexible 3/8" x 1/2" polyethylene cylinder connectors w/ header valves & captive yoke auxiliary cylinder valves | 4 | 0% | 4 | EA | 45 | 285 | 180 | 1140 | 1320
62 | WP-240 §2.01-F; Sh 43 (Dual Cylinder Scale Detail) | 7 | W&T Series 50-345 chlorine cylinder scales (separate operating & standby) with display & J-box | 2 | 0% | 2 | EA | 350 | 4200 | 700 | 8400 | 9100
BOOSTER PUMP & WATER SUPPLY PIPING
63 | WP-240 §2.01-C; Sh 12 Rev. (1 HP booster pump) | 7 | Sta-Rite 1 HP booster pump with bypass piping | 1 | 0% | 1 | EA | 650 | 1450 | 650 | 1450 | 2100
64 | WP-240 §2.01-E; Spec 15100 | 7 | Sch 80 PVC threaded chlorine solution & booster water supply piping, fittings (interior) | 30 | 10% | 33 | LF | 18 | 12 | 594 | 396 | 990
65 | WP-240 §2.01-E | 7 | Hayward Safe Block true-union PVC ball check valves | 17 | 0% | 17 | EA | 45 | 145 | 765 | 2465 | 3230
66 | WP-240 §2.01-E; Sh 12 Rev. (solenoid valve typ) | 7 | Plast-O-Matic EASMD6EP22W28 PVC solenoid control valves | 2 | 0% | 2 | EA | 120 | 950 | 240 | 1900 | 2140
67 | WP-240 §2.01-E; Sh 12 Rev. (strainer) | 7 | Hayward PVC wye strainer w/ 316 SS 40-mesh screen | 1 | 0% | 1 | EA | 85 | 425 | 85 | 425 | 510
68 | WP-240 §2.01-E | 7 | Plast-O-Matic PR0150V pressure regulator valve & RVT150V-PV pressure relief valve (booster pump) | 1 | 0% | 1 | SET | 200 | 1350 | 200 | 1350 | 1550
69 | WP-240 §2.01-E; Sh 12 Rev. (pressure gauge typ) | 7 | Ashcroft 35-1009-SWL-02L pressure gauges, 0 to 160 psi | 1 | 0% | 1 | EA | 45 | 225 | 45 | 225 | 270
CHLORINE GAS PIPING & VENT
70 | WP-240 §2.01-D; Spec 15100 | 7 | Sch 80 PVC threaded chlorine gas manifold & vacuum piping to chlorinators w/ Sch 80 true-union ball valves & fittings | 25 | 10% | 27.5 | LF | 22 | 14 | 605 | 385 | 990
71 | WP-240 §2.01-A; Sh 12 Rev. (route vent pipe to outside) | 7 | Polyethylene chlorine vent tubing from pressure relief valves to building exterior w/ SS screened outlets | 30 | 10% | 33 | LF | 6 | 3 | 198 | 99 | 297
72 | WP-240 §2.01-D (Grinnell 138R / 128R, FH-338) | 7 | Pipe supports & hangers (Grinnell Fig 138R w/ 128R base plates, threaded rods, Phillips FH-338 anchors) | 10 | 0% | 10 | EA | 45 | 65 | 450 | 650 | 1100
INJECTION ASSEMBLIES AT WELL HEADER
73 | Sh 11 (Chemical Solution Injection Assembly; "provide two injection assemblies for each chemical") | 7 | Chemical solution injection assembly at header: W&T S10K diffusion tube, tapped saddle w/ 1" CLS tap, 1" Sch 80 PVC, union, ball valve, galvanized pipe w/ 1" insulation to 6" below grade | 2 | 0% | 2 | EA | 750 | 1650 | 1500 | 3300 | 4800
LEAK DETECTION & SCBA
74 | WP-240 §2.01-G; Sh 12 Rev. Note 2 | 7 | W&T Series 50-135 chlorine gas leak detector, wall-mounted, remote sensor ≤6" AFF in chlorine room, alarm light & aux/fan contacts, 1 lot spares (electrolyte, fuses, lamps) | 1 | 0% | 1 | EA | 650 | 3600 | 650 | 3600 | 4250
75 | WP-240 §2.01-H; Sh 12 Rev. (SCBA weatherproof UV-resistant housing) | 7 | Self-contained breathing apparatus (full face, OSHA) with weatherproof UV-resistant exterior cabinet & ammonia test bottle | 1 | 0% | 1 | EA | 250 | 4200 | 250 | 4200 | 4450
START-UP, TRAINING & SERVICE
76 | WP-240 §7.01, 12.01 | 7 | Manufacturer's inspection, 8-hr start-up, 8-hr operator training & quarterly service visits for 1 year (4 visits) | 1 | 0% | 1 | LS | 6500 | 1000 | 6500 | 1000 | 7500
|  |  | Subtotal | [6 empty] | 16242 | 58500 | 74742
|  | 9 | BID ITEM 9: WELL COLLECTION LINE CONNECTION AT EXISTING WATER WELL NO. 4
INVESTIGATION
77 | Sh 7 (field verify yard piping) | 9 | Field verification / potholing of existing yard piping, valves & appurtenances at Well 4 site | 1 | 0% | 1 | LS | 2200 | 300 | 2200 | 300 | 2500
TIE-IN: TEE, BENDS & THRUST BLOCKS
78 | Sh 7 (Proposed Connection at Well No. 4) | 9 | Cut-in connection to existing 12" well collection line (coordinate operator shutdown; limit shut-down time per Sh 7 Note 1) | 1 | 0% | 1 | LS | 5500 | 1800 | 5500 | 1800 | 7300
79 | Sh 7 | 9 | 12" x 12" DI tee, MJ, cement-mortar lined, with MJ restraint glands | 1 | 0% | 1 | EA | 350 | 1150 | 350 | 1150 | 1500
80 | Sh 7 ((2) 12" 45° bends, M.J.) | 9 | 12" x 45° DI bends, MJ with restraint glands | 2 | 0% | 2 | EA | 225 | 650 | 450 | 1300 | 1750
81 | Sh 17 (Thrust Block Detail) | 9 | Concrete thrust blocks at Well 4 tee & bends | 3 | 0% | 3 | EA | 185 | 165 | 555 | 495 | 1050
GATE VALVES & BOXES
82 | Sh 7; Sh 2 Water Note 6 & 8; Spec 02521 | 9 | 12" resilient-seat gate valve (AWWA C509/C515), MJ, w/ cast iron valve box, extension & concrete collar (Sh 17 Valve Box Detail) | 2 | 0% | 2 | EA | 650 | 3400 | 1300 | 6800 | 8100
RESTORATION
83 | Sh 7 | 9 | Restore existing crushed rock/gravel surfacing & fencing at Well 4 disturbed area | 1 | 0% | 1 | LS | 1200 | 800 | 1200 | 800 | 2000
|  |  | Subtotal | [6 empty] | 11555 | 12645 | 24200
|  | 10 | BID ITEM 10: VARIOUS YARD PIPING
TREATED WATER & CHLORINE SOLUTION LINES IN 2" CARRIER
84 | Sh 14 ((1) 2" PVC conduit for chlorine chemical line) | 10 | 2" Sch 80 PVC carrier conduit for treated water & chlorine solution lines, incl. trench & backfill | 149.44 | 5% | 156.912 | LF | 7.5 | 4.25 | 1176.84 | 666.876 | 1843.716
85 | Sh 5 (Prop 1" treated water tap), Sh 12 Rev. | 10 | 1" Sch 80 PVC treated water supply line from well header tap to chemical room (buried, within 2" carrier) | 86.29 | 10% | 94.919 | LF | 2.25 | 2.1 | 213.5678 | 199.3299 | 412.8977
86 | Sh 5 (Prop 3/4" PVC chemical supply line), Sh 11, 12 Rev.; Spec 15100 | 10 | 3/4" Sch 80 PVC chlorine solution line from chlorinators to well header injection point (Sh 14 elev. notes 1" line, confirm size) | 63.15 | 10% | 69.465 | LF | 2 | 1.75 | 138.93 | 121.5637 | 260.4937
WELL BLOW-OFF
87 | Sh 9 (Item 17 & 11), Sh 11 (Splash Pad) | 10 | Well blow-off discharge to splash pad (via header tee/gate valve/90°, see Group 13) | 1 | 0% | 1 | LS | 1200 | 600 | 1200 | 600 | 1800
|  |  | Subtotal | [6 empty] | 2729.3378 | 1587.7697 | 4317.1074
|  | 11 | BID ITEM 11: CRUSHED CONCRETE DRIVEWAY (925 SY)
CRUSHED CONCRETE DRIVES & WELL SITE
88 | Sh 5, 6, 18 (All-Weather Access Path); Spec 02201 | 11 | Subgrade preparation, proof roll & compaction for drives, well site & laydown area | 924 | 0% | 924 | SY | 1.2 | 0.8 | 1108.8 | 739.2 | 1848
89 | Sh 18 (All-Weather Access Path) | 11 | 6" granular fill (3" x 5" rock) base course, compacted | 154 | 10% | 169.4 | CY | 12 | 42 | 2032.8 | 7114.8 | 9147.6
90 | Sh 18; Spec 02713 | 11 | 3" recycled crushed concrete surface course (RCCB per Spec 02713 min. 7% cement where required), crowned 2% to drain | 77 | 10% | 84.7 | CY | 12 | 36 | 1016.4 | 3049.2 | 4065.6
DRIVEWAY CONNECTION TO CR 5714
91 | Sh 5, 6 (R15' returns at CR 5714) | 11 | Driveway connection / apron to CR 5714 with 15' radius returns, 15' wide drive (Medina County ROW) | 1 | 0% | 1 | EA | 1500 | 1800 | 1500 | 1800 | 3300
|  |  | Subtotal | [6 empty] | 5658 | 12703.2 | 18361.2
|  | 12 | BID ITEM 12: CMU CONTROL & CHEMICAL BUILDING
BUILDING PAD (48" UNDERCUT & SELECT FILL)
92 | Sh 14 Notes 1-3; Geotech Rpt (ARIAS) Tbl 7; Spec 02316 | 12 | Excavate 48" undercut below slab extending 5'-0" beyond slab perimeter | 86 | 0% | 86 | CY | 8 | 6 | 688 | 516 | 1204
93 | Sh 3 Subgrade Prep 4; Sh 14 Note 2-3 | 12 | Proof-roll (20-ton rubber tired), scarify, moisture condition & compact 9" subgrade at base of undercut | 64 | 0% | 64 | SY | 4 | 2 | 256 | 128 | 384
94 | Sh 14 (48" compacted select fill per geotechnical report); Spec 02320 §D | 12 | Select fill (LL<40, PI 10 to 20) placed & compacted to 95% ASTM D1557 to 48" | 86 | 25% | 107.5 | CY | 14 | 28 | 1505 | 3010 | 4515
PERIMETER GRADE BEAM 1'-6" x 3'-0"
95 | Sh 15 (Perimeter Grade Beam 1'-6" W x 3'-0" D) | 12 | Perimeter grade beam 1'-6" x 3'-0", monolithic with slab, 6" chamfer | 8.0556 | 5% | 8.4583 | CY | 350 | 260 | 2960.4167 | 2199.1667 | 5159.5833
96 | Sh 15 (3-#6 top & bottom, std hook each end) | 12 | Reinforcing steel Gr 60, grade beam 6-#6 continuous (3 top / 3 bottom) incl. corner bars & laps | 522.696 | 10% | 574.9656 | LB | 0.8 | 0.95 | 459.9725 | 546.2173 | 1006.1898
97 | Sh 15 (#4 @ 12" stirrups) | 12 | Reinforcing steel Gr 60, grade beam #4 stirrups @ 12" | 349 | 10% | 383.9 | LB | 0.8 | 0.95 | 307.12 | 364.705 | 671.825
98 | Sh 15 (#4 dowel @ 24" max, 24" projection, 18" embed) | 12 | Reinforcing steel Gr 60, #4 CMU dowels @ 24" (match all vertical bars) | 67.802 | 10% | 74.5822 | LB | 0.8 | 0.95 | 59.6658 | 70.8531 | 130.5189
99 | Sh 13 (Prop 1" & 2" wall penetrations); Sh 15 (pipe penetration thru grade beam) | 12 | Sleeves through grade beam / wall for water, chemical & drain lines with watertight link seals (Sh 12 Note 5) | 4 | 0% | 4 | EA | 85 | 185 | 340 | 740 | 1080
SLAB-ON-GRADE 6"
100 | Sh 13 (Slab Plan); Sh 15 (Typical Grade Beam Detail) | 12 | 15-mil continuous vapor retarder under slab & grade beam turn-down | 343.8 | 10% | 378.18 | SF | 0.25 | 0.35 | 94.545 | 132.363 | 226.908
101 | Sh 13 (6" thick slab-on-grade); Sh 3 | 12 | 6" reinforced slab-on-grade 20'-0" x 9'-4", sloped to 4" floor drain in chlorine room (FF -1/2"), MCC FF +1/2" | 3.5 | 5% | 3.675 | CY | 150 | 185 | 551.25 | 679.875 | 1231.125
102 | Sh 13 (6" thick w/ #4 @ 12" OC EW) | 12 | Reinforcing steel Gr 60, slab #4 @ 12" OC each way on chairs @ 24" (Sh 3 Note 9) | 299 | 10% | 328.9 | LB | 0.8 | 0.95 | 263.12 | 312.455 | 575.575
103 | Sh 3 Gen Str Notes 6-8; Sh 13 | 12 | Slab finishing (steel trowel, broom at exterior walks), curing compound / 7-day wet cure | 187 | 0% | 187 | SF | 1.25 | 0.2 | 233.75 | 37.4 | 271.15
104 | Sh 3 Gen Str Note 19 (slip resistant epoxy) | 12 | Slip-resistant epoxy floor coating incl. housekeeping pad & 4" cove | 150 | 10% | 165 | SF | 5.5 | 4.5 | 907.5 | 742.5 | 1650
MCC HOUSEKEEPING PAD
105 | Sh 13 (3'-0" housekeeping pad, FF = 4"); Sh 15 (Housekeeping Pad Detail) | 12 | MCC housekeeping pad 12'-0" x 3'-0" x 4", #4 @ 12" (2 bars min.), 3/4" chamfer, rough construction joint | 1 | 0% | 1 | EA | 450 | 250 | 450 | 250 | 700
8" CMU WALLS (FULLY GROUTED)
106 | Sh 13, 14; Sh 3 Concrete Masonry 1-5; Spec 04200 | 12 | 8" CMU ASTM C90 Gr N normal weight (1,900 psi), smooth or split-face as selected, running bond, Type S mortar, exterior walls, gables & full-height interior wall to roof | 618 | 5% | 648.9 | SF | 8.5 | 4.5 | 5515.65 | 2920.05 | 8435.7
107 | Sh 3 CMU Note 2 / Gen Str Note 12; Sh 14 (fully grouted) | 12 | Masonry grout ASTM C476 (coarse, 2,000 psi per CMU Note 2 / 2,500 psi fine per Gen Note 12, use 2,500 psi), all cells | 6 | 10% | 6.6 | CY | 180 | 225 | 1188 | 1485 | 2673
108 | Sh 15 (#4 vert @ 24" max); Sh 16 (0422-001 corners) | 12 | Reinforcing steel Gr 60, #4 vertical bars @ 24" + 3 cells each corner, full height w/ laps | 211 | 10% | 232.1 | LB | 0.8 | 0.95 | 185.68 | 220.495 | 406.175
109 | Sh 3 Gen Str Note 13; Sh 3 CMU Note 7B | 12 | 3/8" hot-dip galv. ladder-type horizontal joint reinforcing @ 16" OC w/ prefabricated corners, 15" laps | 470 | 10% | 517 | LF | 0.35 | 0.55 | 180.95 | 284.35 | 465.3
110 | Sh 16 (0422-031 CMU Control Joint) | 12 | CMU control joints w/ rubber control joint, backer rod & sealant | 20 | 0% | 20 | LF | 6.5 | 4 | 130 | 80 | 210
111 | Sh 3 Gen Str Note 19; Sh 16 Note (CMU to be painted); Spec 09901 §13.01-B | 12 | Masonry coating system, Tnemec 130 Envirofill + 2 coats 156 Enviro-Crete, CMU interior & exterior faces | 1150 | 10% | 1265 | SF | 1.45 | 0.95 | 1834.25 | 1201.75 | 3036
112 | Sh 3 CMU Notes 9-10 | 12 | Masonry inspection & unit/grout testing (unit strength method) | 1 | 0% | 1 | LS | 1500 | 750 | 1500 | 750 | 2250
BOND BEAM & DOOR LINTELS
113 | Sh 15 (bond beam reinforced w/ cont #5); Sh 16 | 12 | 8" CMU bond beam course at roof level (bond beam units, grouted) | 64 | 5% | 67.2 | LF | 7.5 | 5.5 | 504 | 369.6 | 873.6
114 | Sh 15 (Single Door Opening Reinf.); Sh 16 (W >2'-8" ≤4'-0" to 16" lintel) | 12 | 8" CMU lintel, 16" deep, over 3'-4" rough door openings (A/B/C bars per schedule) | 2 | 0% | 2 | EA | 150 | 125 | 300 | 250 | 550
115 | Sh 15 (bond beam cont #5; lintel 2-#5; jamb 2-#5); Sh 16 (0422-003 schedule) | 12 | Reinforcing steel Gr 60, #5 bond beam continuous, door lintels (2-#5 extended 2'-8") & 2 full-height #5 each jamb | 139.0736 | 10% | 152.981 | LB | 0.8 | 0.95 | 122.3848 | 145.3319 | 267.7167
ROOF FRAMING
116 | Sh 3 Gen Str Note 16; Sh 13 (Roof Framing Plan) | 12 | Pre-engineered wood gable roof trusses @ 24" OC max, 2:12 pitch, incl. gable end trusses, PE-sealed deferred submittal | 186.9 | 0% | 186.9 | SF | 3.5 | 7.5 | 654.15 | 1401.75 | 2055.9
117 | Sh 13 (Gable End Detail: 2x4 look out @ 18") | 12 | 2x4 lookouts @ 18" max at gable ends (1'-0" overhang) & barge rafters | 60 | 0% | 60 | SF | 4.5 | 2.5 | 270 | 150 | 420
118 | Sh 13 (Gable End Detail) | 12 | 2x treated sill / top plate on bond beam w/ anchors, 2x4 treated blocking, ridge & ceiling blocking, 2x4 blocking at gyp. butt joints | 67 | 0% | 67 | LF | 4.5 | 3.25 | 301.5 | 217.75 | 519.25
119 | Sh 13 (Simpson Strong-Tie S/H GAM clip at each truss; metal joist hanger) | 12 | Simpson hurricane clips / GAM clips at each truss bearing & metal joist hangers | 33.5 | 0% | 33.5 | EA | 8 | 6 | 268 | 201 | 469
ROOF SHEATHING & SHINGLES
120 | Sh 3 Gen Str Note 15; Sh 13 & 15 (3/4" roof deck) | 12 | 3/4" wood structural panel roof deck, 48/24 span rating, blocked, 8d nails @ 3"/4"/6" | 251.88 | 10% | 277.068 | SF | 1.25 | 1.85 | 346.335 | 512.5758 | 858.9108
121 | Sh 3 Gen Str Note 20 | 12 | 30-lb roofing felt underlayment | 253 | 10% | 278.3 | SF | 0.2 | 0.15 | 55.66 | 41.745 | 97.405
122 | Sh 3 Gen Str Note 20 | 12 | 30-year architectural asphalt shingles by authorized installer incl. starter course & hip/ridge caps | 253 | 10% | 278.3 | SF | 2.25 | 1.6 | 626.175 | 445.28 | 1071.455
123 | Sh 3 Gen Str Note 20 | 12 | Continuous ridge vent along roof ridge | 22 | 5% | 23.1 | LF | 4 | 5 | 92.4 | 115.5 | 207.9
124 | Sh 13 & 14 (edge of roof) | 12 | Pre-finished metal drip edge at eaves & rakes | 67 | 10% | 73.7 | LF | 1.5 | 1.75 | 110.55 | 128.975 | 239.525
FASCIA, SOFFIT, GUTTERS & DOWNSPOUTS
125 | Sh 3 Gen Str Note 21; Sh 15 (1x4 fascia board) | 12 | James Hardie (or equal) fiber-cement fascia & trim, 1x4, sealed & painted | 67 | 10% | 73.7 | LF | 4.5 | 3.5 | 331.65 | 257.95 | 589.6
126 | Sh 3 Gen Str Note 21; Sh 13 (soffit & molding) | 12 | James Hardie vented fiber-cement soffit, 1'-0" wide at eaves & rakes, w/ molding, sealed & painted | 67 | 10% | 73.7 | SF | 5 | 4 | 368.5 | 294.8 | 663.3
127 | Sh 14 (4" seamless gutters) | 12 | 4" seamless aluminum gutters, both eaves | 44 | 5% | 46.2 | LF | 5.5 | 5.5 | 254.1 | 254.1 | 508.2
128 | Sh 14 (gutter downspouts at corners) | 12 | Aluminum downspouts w/ elbows & concrete splash blocks (4 locations x ±10') | 43 | 5% | 45.15 | LF | 5.5 | 6.5 | 248.325 | 293.475 | 541.8
GYPSUM CEILING & ATTIC INSULATION
129 | Sh 3 Gen Str Note 18; Sh 13 (5/8" gypsum brd panels) | 12 | 5/8" gypsum board ceiling screwed to truss bottom chords, taped, floated & textured (chlorine room 6'x8' + MCC 12'x8') | 144 | 10% | 158.4 | SF | 2.25 | 1.1 | 356.4 | 174.24 | 530.64
130 | Sh 3 Gen Str Note 18-19 | 12 | Paint gypsum ceilings (primer + 2 coats, moisture/chemical resistant) | 144 | 10% | 158.4 | SF | 1.2 | 0.5 | 190.08 | 79.2 | 269.28
131 | Sh 3 Gen Str Note 22 | 12 | R-30 attic insulation above ceiling (batt or blown) | 144 | 10% | 158.4 | SF | 0.55 | 0.95 | 87.12 | 150.48 | 237.6
132 | Sh 12 Rev. (interior wall to span all the way to roof) | 12 | Seal top of interior CMU chlorine-room wall to roof deck (gas-tight, fire/smoke sealant) | 12 | 0% | 12 | LF | 8 | 6 | 96 | 72 | 168
DOORS & HARDWARE
133 | Sh 12 Rev. Door Schedule (101B, count 2); Sh 3 Note 17 & Sh 15 (steel/SS HM frame), schedule governs | 12 | Chemical-resistant FRP door 3'-0" x 6'-10" w/ 2'x2' vision lite & FRP frame, grouted, sealant both sides | 2 | 0% | 2 | EA | 700 | 2900 | 1400 | 5800 | 7200
134 | Sh 12 Rev. Notes & Door Schedule; Sh 14; Sh 29 (keyed note 4 crash bar) | 12 | Door hardware set: panic (crash) bar, lever trim, heavy-duty wind spring & chain, SS hinges, security hasp w/ padlock, weatherstripping, threshold, ADA operable (Sh 12 Note 10) | 2 | 0% | 2 | SET | 250 | 1150 | 500 | 2300 | 2800
135 | Sh 12 Rev. Note 5 | 12 | Joint sealants at door frames & wall penetrations | 80 | 10% | 88 | LF | 1.1 | 0.65 | 96.8 | 57.2 | 154
LOUVERS
136 | Sh 12 Rev. Note 8; Sh 14 West Elev. (exhaust louver with insect screen) | 12 | Chlorine room exhaust louver ≤1'-0" AFF, secluded from working area, corrosion resistant w/ insect screen & backdraft damper | 1 | 0% | 1 | EA | 250 | 850 | 250 | 850 | 1100
137 | Sh 14 South Elev. (control room exhaust louver w/ insect screen) | 12 | Control (MCC) room exhaust louver with insect screen | 1 | 0% | 1 | EA | 200 | 550 | 200 | 550 | 750
PIPE BOLLARDS
138 | Sh 12 Rev. (prop conc bollard, see Sh 18); Sh 15 (Bollard Detail); Sh 28 keyed note 5 | 12 | 8" std. steel pipe bollards, concrete filled, painted yellow, 4' above grade in 18" dia x 4' concrete base, around building & equipment | 10 | 0% | 10 | EA | 350 | 450 | 3500 | 4500 | 8000
PIPE IDENTIFICATION
139 | Sh 12 Rev. Note 11 | 12 | Chemical piping flow-direction labeling & pipe identification | 1 | 0% | 1 | LS | 450 | 350 | 450 | 350 | 800
BUILDING DRAIN LINE TO DAYLIGHT
140 | Sh 5, 8, 13, 14; Sh 12 Rev. | 12 | 4" PVC Sch 40 drain line from chlorine room floor drain to daylight (FL 769.25) | 40.52 | 5% | 42.546 | LF | 9 | 6 | 382.914 | 255.276 | 638.19
141 | Sh 8 (drain to daylight) | 12 | Outfall protection at 4" drain daylight (rock/riprap splash, rodent screen) | 1 | 0% | 1 | EA | 250 | 300 | 250 | 300 | 550
|  |  | Subtotal | [6 empty] | 32223.9137 | 37189.4088 | 69413.3225
|  | 13 | BID ITEM 13: 12-INCH CMP CULVERT (45 LF)
12" CMP CULVERT WITH SAFETY END TREATMENTS
142 | Sh 5, 8; Spec 02511 | 13 | 12" corrugated metal pipe (CMP) culvert under CR 5714 driveway incl. excavation, bedding & backfill | 45 | 0% | 45 | LF | 18 | 28 | 810 | 1260 | 2070
143 | Sh 19 (TxDOT SETP-PD Type II) | 13 | Safety end treatment Type II parallel drainage, cast-in-place, 12" CMP (6:1 slope, mitered ends), no cross pipes req'd for 12" | 2 | 0% | 2 | EA | 1400 | 1100 | 2800 | 2200 | 5000
144 | Sh 19 (Cross pipe table: 12" = 0.6 CY/end) | 13 | Concrete riprap & toewall at SETs (0.6 CY per end per TxDOT table) | 1.2 | 10% | 1.32 | CY | 450 | 350 | 594 | 462 | 1056
|  |  | Subtotal | [6 empty] | 4204 | 3922 | 8126
|  | 14 | BID ITEM 14: DRILL 1ST PILOT HOLE WITH GEOPHYSICAL LOG (1,890 VF)
PILOT HOLE 0' TO 1,890' & GEOPHYSICAL LOG
145 | Sh 10; Spec 13200 §3.03 | 14 | 1st pilot/test hole, mud rotary, 7-7/8" to 9-7/8" bit, 0' to 1,890' incl. driller's log, 10-ft cutting samples (3 sets), drift readings @ ±30', mud program w/ portable tanks & desander (no earthen pits) | 1890 | 0% | 1890 | VF | 50 | 25 | 94500 | 47250 | 141750
146 | Spec 13200 §3.04(i) | 14 | Geophysical log set #1 at ±1,890' (induction/resistivity, SP, caliper, natural gamma, spectral gamma, density-neutron porosity) | 1 | 0% | 1 | EA | 6000 | 3500 | 6000 | 3500 | 9500
|  |  | Subtotal | [6 empty] | 100500 | 50750 | 151250
|  | 15 | BID ITEM 15: DRILL 2ND PILOT HOLE WITH GEOPHYSICAL LOG, 1,890 TO 2,520 FT (630 VF)
PILOT HOLE 1,890' TO 2,520' & GEOPHYSICAL LOG
147 | Spec 13200 §3.03 | 15 | 2nd pilot hole continuing from 1,890' to 2,520' (Edwards Aquifer) incl. samples & drift readings | 630 | 0% | 630 | VF | 60 | 30 | 37800 | 18900 | 56700
148 | Spec 13200 §3.04(ii) | 15 | Geophysical log set #2 at total depth ±2,520' | 1 | 0% | 1 | EA | 7000 | 4000 | 7000 | 4000 | 11000
149 | Spec 13200 §3.04 to 3.05 | 15 | Professional log evaluation (gas / radioactivity) & Contractor Test Hole Evaluation Report with well completion recommendations | 1 | 0% | 1 | LS | 6500 | 0 | 6500 | 0 | 6500
|  |  | Subtotal | [6 empty] | 51300 | 22900 | 74200
|  | 16 | BID ITEM 16: 30-SACK CEMENT PLUG IN PILOT TEST HOLE
CEMENT PLUG
150 | Spec 13200 §3.07 | 16 | 30-sack Portland cement plug in pilot hole below total depth of well (15 ppg slurry via drill pipe), 24-hr cure & 6,000-lb tag test | 1 | 0% | 1 | EA | 2800 | 1200 | 2800 | 1200 | 4000
|  |  | Subtotal | [6 empty] | 2800 | 1200 | 4000
|  | 17 | BID ITEM 17: 2-PIECE 16-INCH x 10-INCH WATER WELL (CASING, CEMENTING, OPEN HOLE, CLEANING, DISINFECTION, VIDEO SURVEY)
26" SURFACE CASING (0' TO 40')
151 | Sh 10 (30" dia borehole 0'-40') | 17 | Ream 30" dia borehole for surface casing, 0' to 40' | 40 | 0% | 40 | VF | 200 | 100 | 8000 | 4000 | 12000
152 | Sh 10 (26" x 0.375" steel surface casing, cemented 0'-40') | 17 | 26" OD x 0.375" wall steel surface casing, set & cemented 0' to 40' (not listed on Bid Form Item 17, shown on Sh 10) | 40 | 5% | 42 | LF | 35 | 105 | 1470 | 4410 | 5880
153 | Sh 10; Spec 13200 §2.05 | 17 | Cement surface casing annulus (Class A w/ ≤6% gel, 13.5 ppg) | 35 | 0% | 35 | SACK | 20 | 35 | 700 | 1225 | 1925
16" CONDUCTOR CASING (0' TO 802')
154 | Sh 10 (22" dia borehole 40'-840'); Spec 13200 §3.09 | 17 | Stage pilot-ream 22" dia borehole, 40' to 840' (min. 6" larger than 16" casing OD) | 800 | 0% | 800 | VF | 85 | 45 | 68000 | 36000 | 104000
155 | Spec 13200 §3.09 | 17 | Continuous (gyro / Baker) alignment survey of reamed hole @ ≤15' intervals, plotted report, before conductor casing | 1 | 0% | 1 | EA | 3500 | 1000 | 3500 | 1000 | 4500
156 | Sh 10 (16" x 0.500" steel casing +2'-800'); Spec 13200 §2.04, 3.10 | 17 | 16" OD x 0.500" wall API 5L / ASTM A53 Gr B steel conductor casing, beveled, AWWA C206 field welded, +2' (36" stick-up per §3.10) to 800' | 802 | 2% | 818.04 | LF | 37 | 105 | 30267.48 | 85894.2 | 116161.68
157 | Sh 10 (centralizers @ 100' intervals); Spec 13200 §2.07, 3.10 | 17 | Casing centering guides (1/4" x 2" bowed steel, sets of 4) on 16" casing @ ±80' + first set 4' above bottom | 11 | 0% | 11 | SET | 75 | 275 | 825 | 3025 | 3850
158 | Sh 10 (16" x 10" swage 800'-802') | 17 | 16" x 10-3/4" welded steel swage (800' to 802') | 1 | 0% | 1 | EA | 450 | 1850 | 450 | 1850 | 2300
10-3/4" CASING (802' TO 1,890')
159 | Sh 10 (16" dia borehole 840'-1,890') | 17 | Ream 16" dia borehole for 10-3/4" casing, 840' to 1,890' | 1050 | 0% | 1050 | VF | 65 | 35 | 68250 | 36750 | 105000
160 | Sh 10 (10-3/4" x 0.500" steel casing 802'-1,890'); Spec 13200 §2.06 | 17 | 10-3/4" OD x 0.500" wall API 5L / A53 Gr B steel casing (blank liner), beveled & field welded, 802' to 1,890' | 1088 | 2% | 1109.76 | LF | 28 | 68 | 31073.28 | 75463.68 | 106536.96
161 | Sh 10; Spec 13200 §2.07, 3.12 | 17 | Balloon-type centralizers (Weatherford/Antelope) on 10-3/4" casing @ 100' intervals | 10 | 0% | 10 | EA | 60 | 240 | 600 | 2400 | 3000
PRESSURE CEMENTING (0' TO 1,890')
162 | Spec 13200 §3.11 (AWWA A100 App. C) | 17 | Float shoe / back-pressure valve, cementing head & plug | 1 | 0% | 1 | EA | 1500 | 4500 | 1500 | 4500 | 6000
163 | Sh 10 (Pressure cement 0'-1,890'); Spec 13200 §2.05, 3.11 | 17 | Pressure cementing of casing string 0' to 1,890' through float shoe by qualified cementing co., Class A w/ ≤6% bentonite (13.5 ppg), 36-hr set, W-15 report | 1380 | 0% | 1380 | SACK | 18 | 27 | 24840 | 37260 | 62100
8-3/4" OPEN HOLE (1,890' TO 2,520')
164 | Bid Item 17 (Addendum 1: 8-3/4" open hole); Addendum 1 Clar. 6 | 17 | Drill-out of cement/shoe & complete 8-3/4" open hole 1,890' to 2,520' (Addendum 1 governs over 9-7/8" on Sh 10 / Spec §1.06) | 630 | 0% | 630 | VF | 62 | 33 | 39060 | 20790 | 59850
WELL CLEANING & DEVELOPMENT
165 | Spec 13200 §3.14 | 17 | Well cleaning / development with drilling rig: mud-removal chemicals, tandem agitator, air-lift & backwashing (min. 24 hrs) | 24 | 0% | 24 | HR | 450 | 200 | 10800 | 4800 | 15600
166 | Spec 13200 §3.14 | 17 | Sound bottom & clean-out of fill >5' above back-pressure valve prior to test pump | 1 | 0% | 1 | LS | 3500 | 500 | 3500 | 500 | 4000
VIDEO SURVEY, DISINFECTION & PROTECTION
167 | Spec 13200 §3.26 | 17 | Color well video survey (side-view) of entire well with digital copy & written report | 1 | 0% | 1 | EA | 3800 | 1000 | 3800 | 1000 | 4800
168 | Spec 13200 §3.27; Sh 2 TCEQ Note 6f | 17 | Well disinfection per AWWA C654 (disinfectant in well ≥12 hrs per Sh 2), flushing & 3 successive daily coliform-free samples | 1 | 0% | 1 | LS | 2500 | 1500 | 2500 | 1500 | 4000
169 | Spec 13200 §3.24 | 17 | Temporary well protection, welded steel plate on casing between test pump removal & permanent pump | 1 | 0% | 1 | EA | 400 | 350 | 400 | 350 | 750
RECORDS & REPORTS
170 | Spec 13200 §1.04-B, 3.29 | 17 | Well construction records, State of Texas Water Well Report, cementing tables, mill & welder certs, sieve analysis & drilling-mud arsenic testing | 1 | 0% | 1 | LS | 3500 | 0 | 3500 | 0 | 3500
DRILLING WATER & CONTAINMENT
171 | Addendum 1 Clar. 2; Spec 13200 §1.02-E | 17 | Drilling water supply from Well No. 4 (hose across ground or temp. connection) incl. chlorination to 0.5 mg/L residual & meter if required | 1 | 0% | 1 | LS | 3500 | 2500 | 3500 | 2500 | 6000
172 | Addendum 1 Clar. 2 & 4 (holding/frac tanks recommended) | 17 | On-site water holding / frac tanks for drilling water & discharge containment (rental incl. delivery & removal) | 6 | 0% | 6 | MO | 400 | 3600 | 2400 | 21600 | 24000
WASTE DISPOSAL & NOISE CONTROL
173 | Spec 13200 §1.02-H; Addendum 1 Clar. 4 | 17 | Legal off-site disposal of drilling mud, cuttings & fluids (no runoff to neighboring properties) | 250 | 0% | 250 | CY | 30 | 55 | 7500 | 13750 | 21250
174 | Spec 13200 §1.04-B item 20 | 17 | Temporary sound attenuation wall around drilling rig (submittal item 20) | 1 | 0% | 1 | LS | 8500 | 9500 | 8500 | 9500 | 18000
|  |  | Subtotal | [6 empty] | 324935.76 | 370067.88 | 695003.64
|  | 18 | BID ITEM 18: 1,500 GPM TEST LINE SHAFT PUMP & PUMPING TESTS
TEST PUMP & DEVELOPMENT PUMPING
175 | Spec 13200 §3.15 | 18 | Furnish, install & remove 1,500 GPM line-shaft test pump @ 350 TDH, 600' setting, temp. discharge head, column, auxiliary engine, flow valve, calibrated orifice (12' straight run), Rossum sand sampler & sample cock | 1 | 0% | 1 | LS | 35000 | 25000 | 35000 | 25000 | 60000
176 | Spec 13200 §3.14 (min. 16 hrs w/ test pump) | 18 | Development pumping with test pump incl. development tests at various rates | 16 | 0% | 16 | HR | 275 | 150 | 4400 | 2400 | 6800
STEP & 36-HOUR PRODUCTION TESTS
177 | Spec 13200 §3.16 | 18 | Step drawdown tests, 4 steps x (3 hr pumping + 3 hr recovery), 15-min readings | 24 | 0% | 24 | HR | 275 | 150 | 6600 | 3600 | 10200
178 | Spec 13200 §3.16 | 18 | Pre-test shutdown (12 hr) & post-step recovery water-level monitoring (18 hr min.) | 30 | 0% | 30 | HR | 100 | 20 | 3000 | 600 | 3600
179 | Spec 13200 §3.16; TCEQ 290.41 | 18 | 36-hour continuous production (constant-rate) test incl. 12-hr recovery measurements & Engineer's forms | 48 | 0% | 48 | HR | 275 | 150 | 13200 | 7200 | 20400
180 | Spec 13200 §3.20 to 3.22 | 18 | Pumping test data evaluation, well efficiency (75% guarantee) & suspended solids (≤5 mg/L) documentation | 1 | 0% | 1 | LS | 5500 | 0 | 5500 | 0 | 5500
DISCHARGE WATER MANAGEMENT
181 | Addendum 1 Clar. 4; Sh 2 Hyper-Chlorinated Water Notes | 18 | Temporary discharge piping / hoses to on-site discharge area with energy dissipation (no off-site runoff) | 1 | 0% | 1 | LS | 4500 | 3500 | 4500 | 3500 | 8000
WATER QUALITY TESTING
182 | Spec 13200 §3.14 | 18 | Preliminary chemical analysis during development (pH, TDS, Cl, SO4, hardness, SpC, As, Fe, Mn, F, color, turbidity) | 1 | 0% | 1 | EA | 150 | 650 | 150 | 650 | 800
183 | Spec 13200 §3.17; §3.27 | 18 | Bacteriological analyses, 3 successive days during step & 36-hr tests | 3 | 0% | 3 | EA | 75 | 85 | 225 | 255 | 480
184 | Spec 13200 §3.18 (TCEQ 290.104-.108, .117) | 18 | Full chemical & metals analysis after 36-hr test (IOC, SOC, VOC, metals) incl. additional/dissolved analyses, free ammonia field test, PCE/TCE, H2S, 3 back-up samples | 1 | 0% | 1 | EA | 300 | 4200 | 300 | 4200 | 4500
185 | Spec 13200 §3.19 (TCEQ 290.108) | 18 | Radionuclide analysis (gross alpha, Ra-226, Ra-228, beta, uranium) | 1 | 0% | 1 | EA | 150 | 950 | 150 | 950 | 1100
|  |  | Subtotal | [6 empty] | 73025 | 48355 | 121380
|  | 19 | BID ITEM 19: 1,400 GPM PERMANENT LINE SHAFT PUMP & 400 HP MOTOR
PUMP BOWL ASSEMBLY
186 | Sh 10; Spec 13200 §2.09 | 19 | Vertical turbine oil-lubricated multi-stage pump bowl assembly, 1,400 GPM @ 808' TDH, ≤1,700 rpm, ≥82% bowl eff., ≤12.4" OD, porcelain-enamel lined bowls, lead-free bronze impellers, 416 SS shaft | 1 | 0% | 1 | EA | 0 | 65000 | 0 | 65000 | 65000
187 | Spec 13200 §2.09, 3.31 (HI 14.6 Gr 1B) | 19 | Certified non-witness factory pump bowl test & report | 1 | 0% | 1 | EA | 0 | 3500 | 0 | 3500 | 3500
400 HP MOTOR & ENCLOSURE
188 | Sh 10, 11; Spec 13200 §2.21 | 19 | 400 HP vertical hollow shaft motor, 460V/3Ø/60Hz, 4-pole, premium eff., WP-1, 1.15 SF, non-reverse ratchet, 180% thrust bearings, Class F, 2 space heaters, 6 winding + 2 bearing RTDs | 1 | 0% | 1 | EA | 0 | 62000 | 0 | 62000 | 62000
189 | Sh 11 (Motor Enclosure by Monitor or equal); Addendum 1 Clar. 3 | 19 | Motor enclosure (Monitor or equal) for standard motor casing | 1 | 0% | 1 | EA | 1200 | 9500 | 1200 | 9500 | 10700
DISCHARGE HEAD
190 | Spec 13200 §2.10 | 19 | Fabricated steel discharge head w/ ANSI 150 FF flange, base plate, lifting lugs, tension nut/plate, 1-1/2" & 2-1/2" taps, hydrotested | 1 | 0% | 1 | EA | 0 | 14000 | 0 | 14000 | 14000
191 | Spec 13200 §2.10, 2.21 | 19 | Reed critical frequency analysis (motor + discharge head) with written report | 1 | 0% | 1 | EA | 0 | 2500 | 0 | 2500 | 2500
COLUMN PIPE, LINE SHAFT & OIL TUBE
192 | Sh 10 (10-3/4" x 0.365" steel discharge pipe +2'-600'); Spec 13200 §2.11 | 19 | 10-3/4" OD x 0.365" wall API 5L / A53 Gr B T&C column pipe, ≤20' joints, extra-strong sleeve couplings | 602 | 0% | 602 | LF | 0 | 60 | 0 | 36120 | 36120
193 | Spec 13200 §2.12 | 19 | C1045 line shaft, ≤20' interchangeable sections, machined couplings | 600 | 0% | 600 | LF | 0 | 32 | 0 | 19200 | 19200
194 | Spec 13200 §2.13 | 19 | Sch 80 steel oil tube (≤5' sections) w/ bronze bearings & rubber spiders @ 40' max, tension nut & plate | 600 | 0% | 600 | LF | 0 | 28 | 0 | 16800 | 16800
195 | Spec 13200 §2.14 | 19 | Pump suction pipe & stainless steel cone strainer | 1 | 0% | 1 | EA | 0 | 2800 | 0 | 2800 | 2800
AIR LINE, SOUNDER & CHEMICAL TUBING
196 | Spec 13200 §2.18, 3.31 | 19 | Air-line tubing, 1/4" OD SS, PVC coated (Dekoron 1005-44204), single continuous length, taped @ 20' | 602 | 0% | 602 | LF | 0.75 | 4.5 | 451.5 | 2709 | 3160.5
197 | Spec 13200 §2.18, 3.31 | 19 | Air-line pressure gauge 4-1/2" (ft H2O & psi) w/ Crouse-Hinds CGB 293 connector & test connection | 1 | 0% | 1 | EA | 150 | 450 | 150 | 450 | 600
198 | Sh 10 (1" PVC E-line, perforated last 20'); Spec 13200 §2.17 (1-1/4" Sch 40) | 19 | Electric sounder / water-level monitor tubing, PVC (Spec: 1-1/4" Sch 40 min.; Sh 10: 1") w/ bottom cap & 20' perforations, strapped @ 20' | 602 | 0% | 602 | LF | 0.75 | 3.25 | 451.5 | 1956.5 | 2408
199 | Bid Item 19 (chemical insertion tubing) | 19 | Chemical insertion tubing (listed on Bid Form Item 19; not detailed, size/material to be confirmed by RFI) | 602 | 0% | 602 | LF | 0.75 | 3.5 | 451.5 | 2107 | 2558.5
WELL HEAD ACCESSORIES
200 | Spec 13200 §2.15 | 19 | Oil lubricator, 3 gal reservoir, 150 W 120 V immersion heater w/ thermostat, NEMA 4 solenoid w/ bypass, toggle valve, 1/4" Cu tubing, locking hasp; initial turbine oil fill | 1 | 0% | 1 | EA | 350 | 1850 | 350 | 1850 | 2200
201 | Spec 13200 §2.16; Sh 9 Item 12; Sh 2 TCEQ Note 10 | 19 | Sanitary well seal w/ 2" gooseneck casing vent (#16 mesh 316 SS screen, facing down), relief valve & sampling tap | 1 | 0% | 1 | EA | 350 | 950 | 350 | 950 | 1300
INSTALLATION & FIELD TESTING
202 | Spec 13200 §3.31 | 19 | Installation of permanent pump & motor by TDLR-licensed pump installer (service rig/crane), alignment & start-up | 1 | 0% | 1 | LS | 28000 | 4000 | 28000 | 4000 | 32000
203 | Spec 13200 §3.31 (G-M Services or equal) | 19 | Independent field testing of well & pumping equipment at 3 rates (ultrasonic flow, power analyzer, vibration), report | 1 | 0% | 1 | LS | 4500 | 500 | 4500 | 500 | 5000
204 | Spec 13200 §3.31 | 19 | Bacteriological sample after 4 hrs pumping at guaranteed rate | 1 | 0% | 1 | EA | 75 | 85 | 75 | 85 | 160
|  |  | Subtotal | [6 empty] | 35979.5 | 246027.5 | 282007
|  | 20 | BID ITEM 20: WELL DISCHARGE PIPING, FITTINGS, SUPPORTS & FOUNDATIONS
WELL PUMP FOUNDATION & SEALING SLAB
205 | Sh 11 (Well Pump Foundation Plan/Elev.); Sh 8 (Well Head Grading); Sh 2 TCEQ Note 9 | 20 | Reinforced concrete well pump foundation pedestal, 3'-0" min. each side of casing, 2'-0" above FG x 2'-0" below, 4,000 psi | 1.8519 | 5% | 1.9444 | CY | 650 | 450 | 1263.8889 | 875 | 2138.8889
206 | Sh 10, 11 (6" min seal slab, 1/4"/ft slope, 10'x10') | 20 | Concrete sealing slab 10'-0" x 10'-0" x 6" min. with 6" x 8" edge curb, sloped 1/4"/ft away from casing | 2.1 | 5% | 2.205 | CY | 500 | 380 | 1102.5 | 837.9 | 1940.4
207 | Sh 11 (#4 @ 18" EW; 12-#4 bars; #5 spiral @ 6"); Spec 13200 §3.25 (#5 @ 12" EW EF) | 20 | Reinforcing steel Gr 60, seal slab (priced per Spec §3.25 #5@12" EW each face, more stringent than Sh 11 #4@18"), 12-#4 verticals & #5 spiral @ 6" in pedestal | 380 | 10% | 418 | LB | 0.85 | 0.95 | 355.3 | 397.1 | 752.4
208 | Sh 9 & 11 (1"-648 epoxy grout, Ceilcote) | 20 | 1" Ceilcote 648 epoxy grout under discharge head base plate | 9 | 10% | 9.9 | SF | 45 | 85 | 445.5 | 841.5 | 1287
209 | Sh 11 | 20 | SS anchor bolts for discharge head base plate (template set) | 4 | 0% | 4 | EA | 45 | 85 | 180 | 340 | 520
12" HEADER PIPE, SPOOLS & FITTINGS
210 | Sh 9 Item 2 | 20 | 12" Dresser-style coupling (restrained) at discharge head | 1 | 0% | 1 | EA | 250 | 1650 | 250 | 1650 | 1900
211 | Sh 9 Item 4 | 20 | 12" DI spool piece FE/PE, min. 1' long, with 2" tap (treated water / cut-off switch) | 1 | 0% | 1 | EA | 200 | 1100 | 200 | 1100 | 1300
212 | Sh 9 Item 14 | 20 | 12" DI spool piece PE/FE | 1 | 0% | 1 | EA | 200 | 900 | 200 | 900 | 1100
213 | Sh 9 Item 15 (typ.) | 20 | 12" DI flanged spool pieces FE/FE, various lengths (±30 LF total across header) | 4 | 0% | 4 | EA | 250 | 1500 | 1000 | 6000 | 7000
214 | Sh 9 Item 10 | 20 | 12" x 12" DI tee FE/FE/FE | 1 | 0% | 1 | EA | 300 | 1650 | 300 | 1650 | 1950
215 | Sh 9 Item 13 | 20 | 12" x 45° DI bend FE/FE | 2 | 0% | 2 | EA | 225 | 1050 | 450 | 2100 | 2550
216 | Sh 9 Item 17 | 20 | 12" x 90° DI bend FE/FE (blow-off to splash pad) | 1 | 0% | 1 | EA | 225 | 1150 | 225 | 1150 | 1375
217 | Sh 9 (flange joints) | 20 | 12" flange gasket & bolt sets (ANSI 150, SS/coated bolts) | 18 | 0% | 18 | SET | 45 | 120 | 810 | 2160 | 2970
218 | Sh 9 Note 1; Spec 09901 §13.01-A | 20 | Epoxy coating system A on above-ground header piping, valves & fittings (Tnemec 90-97 / 27WB / 740, SSPC SP-10 blast) | 250 | 10% | 275 | SF | 9 | 4 | 2475 | 1100 | 3575
219 | Sh 9 Note 2 | 20 | 1" fiberglass pipe insulation w/ ASJ and 0.016" embossed aluminum jacket on above-ground header piping & fittings | 45 | 10% | 49.5 | LF | 14 | 18 | 693 | 891 | 1584
HEADER VALVES & FLOW METER
220 | Sh 9 Item 6 | 20 | 12" silent (globe-style) check valve, FE/FE | 1 | 0% | 1 | EA | 450 | 3800 | 450 | 3800 | 4250
221 | Sh 9 Item 11; Spec 02521 | 20 | 12" resilient-seat gate valve, FE/FE, handwheel (above-ground, open CCW) | 2 | 0% | 2 | EA | 450 | 3200 | 900 | 6400 | 7300
222 | Sh 9 Item 8; Spec 13200 §2.19, 13420; Sh 41 | 20 | 12" magnetic flowmeter FE/FE (min. 5' downstream of check valve), transmitter w/ display, Ethernet/Modbus/serial outputs, sun cover | 1 | 0% | 1 | EA | 650 | 9500 | 650 | 9500 | 10150
HEADER INSTRUMENTS & SMALL PIPING
223 | Sh 9 Item 3; Sh 41 (Pressure Switch Mounting Detail) | 20 | Mercoid Series DA high-pressure cut-off switch (DRW-33-153L-7) w/ snubber, SS shut-off valve & 1/2" SS nipple | 1 | 0% | 1 | EA | 150 | 950 | 150 | 950 | 1100
224 | Sh 9 Item 5; Sh 2 TCEQ Note 16 | 20 | 1" air release & vacuum valve with 16-mesh corrosion-resistant screened outlet | 1 | 0% | 1 | EA | 150 | 650 | 150 | 650 | 800
225 | Sh 9 Item 7 | 20 | Pressure gauge 0 to 100 psi w/ isolation valve & snubber | 1 | 0% | 1 | EA | 45 | 185 | 45 | 185 | 230
226 | Sh 9 Item 16; Sh 2 TCEQ Note 12 | 20 | 1" sample tap / hose bib on discharge pipe ahead of treatment | 1 | 0% | 1 | EA | 45 | 95 | 45 | 95 | 140
CONCRETE PIPE SUPPORTS
227 | Sh 9 & 11 (Pipe Support Detail; Sh 15 Pipe Support Saddle) | 20 | Concrete pipe supports, 18" wide, 3'-0" above FG, 2'-8" below, 8" footing, #4 @ 6" & 9", felt pad, HDG 1/4"x2" strap & 5/8" anchors | 2 | 0% | 2 | EA | 650 | 450 | 1300 | 900 | 2200
SPLASH PAD
228 | Sh 9 & 11 (Splash Pad Detail) | 20 | Concrete splash pad 4'-0" x 3'-0" inside, 6" walls & slab, 1'-6" high walls, #4 @ 12" OC EW | 1 | 0% | 1 | EA | 1100 | 750 | 1100 | 750 | 1850
|  |  | Subtotal | [6 empty] | 14740.1889 | 45222.5 | 59962.6889
|  | 21 | BID ITEM 21: ACIDIZATION (10,000 GAL 28% HCL & 60,000 GAL WATER)
ACID & WATER
229 | Spec 13200 §1.02-G | 21 | 28% hydrochloric acid (NSF 60) with phosphate-free wetting agent & inhibitor, delivered | 10000 | 0% | 10000 | GAL | 0 | 2.25 | 0 | 22500 | 22500
230 | Spec 13200 §1.02-G | 21 | Water for acid flush/purging (5,000 gal first flush + remainder), supply & transport | 60000 | 0% | 60000 | GAL | 0.02 | 0.02 | 1200 | 1200 | 2400
ACID INJECTION
231 | Spec 13200 §1.02-G.4 | 21 | 2-7/8" tremie pipe set @ ±600', install & remove | 600 | 0% | 600 | LF | 6 | 4 | 3600 | 2400 | 6000
232 | Spec 13200 §1.02-G.4 | 21 | Pressure acid injection services in 2 stages (3,000 gal + 5,000 gal flush; 2 to 4 hr dwell; 7,000 gal + flush) & 48-hr soak | 1 | 0% | 1 | LS | 18000 | 6000 | 18000 | 6000 | 24000
POST-ACID PUMPING & NEUTRALIZATION
233 | Spec 13200 §1.02-G.4 | 21 | Post-acid pumping to ground/containment until no inhibitor, no sand & pH > 6.0; lab report on inhibitor | 24 | 0% | 24 | HR | 275 | 150 | 6600 | 3600 | 10200
234 | Addendum 1 Clar. 4 | 21 | Spent acid water containment & neutralization (frac tanks, soda ash) prior to discharge on site | 1 | 0% | 1 | LS | 6000 | 8500 | 6000 | 8500 | 14500
|  |  | Subtotal | [6 empty] | 35400 | 44200 | 79600
|  | 22 | BID ITEM 22: REMOVABLE WELL PROTECTION FENCING, WATER WELL NO. 5 (64 LF)
FENCE LINE (FABRIC, REMOVABLE POSTS, FOOTINGS & SCREEN)
235 | Sh 5, 20 (Remote Well No. 5 Site, 16'x16') | 22 | 8'-0" high chain link well protection fence, 1-5/8" center brace & top rail, 7 ga tension wire, 3/8" tension rods | 64 | 0% | 64 | LF | 9.5 | 12.5 | 608 | 800 | 1408
236 | Sh 20 (Removable Post Detail) | 22 | 4" OD removable terminal/line posts (HSS 4.500" x 0.188" A500 Gr B sleeve), 11/16" holes & 5/8" thru bolts w/ saddle washers, in 18" dia x 4'-0" Class "CB" footings @ 8'-0" max | 18 | 0% | 18 | EA | 185 | 245 | 3330 | 4410 | 7740
237 | Sh 20 & 21 (FenceScreen Privacy Plus 200 series, 90%) | 22 | Commercial PVC-coated privacy mesh screen (90% blockage), grommets @ 24", full fence height | 1152 | 5% | 1209.6 | SF | 0.55 | 0.85 | 665.28 | 1028.16 | 1693.44
GATE & PIPE OPENING
238 | Sh 20 (Elevation, with Gate) | 22 | Pedestrian gate 4'-0" x 8'-0", 1.9" OD frame, single gate latch Type 71 | 1 | 0% | 1 | EA | 250 | 650 | 250 | 650 | 900
239 | Sh 20 (Elevation, with Opening) | 22 | Fence panel with framed pipe opening (2'-0" clear, 1-5/8" intermediate braces) | 1 | 0% | 1 | EA | 200 | 250 | 200 | 250 | 450
|  |  | Subtotal | [6 empty] | 5053.28 | 7138.16 | 12191.44
|  | 24 | BID ITEM 24: GENERATOR HOUSEKEEPING PAD ONLY (STRUCTURAL; GENERATOR & GAS EXCLUDED, MEP)
GENERATOR PAD 12"
240 | Sh 47 (10" select backfill 95%); Sh 13 (Generator Foundation, excavate & replace) | 24 | Excavate & replace subgrade with select fill, 95% compaction, under pad & apron | 11 | 25% | 13.75 | CY | 22 | 30 | 302.5 | 412.5 | 715
241 | Sh 47 (6 mil polyethylene barrier) | 24 | 6-mil polyethylene barrier between soil & concrete | 152.72 | 10% | 167.992 | SF | 0.2 | 0.15 | 33.5984 | 25.1988 | 58.7972
242 | Sh 47 (12" pad, 18" thickened edges, enclosure +2" all sides / +6" per Sh 24 Note 11) | 24 | Generator housekeeping pad 12" thick, 4,000 psi, 18" thickened edges, sloped 2% max, 2" AFG | 6.5 | 5% | 6.825 | CY | 260 | 220 | 1774.5 | 1501.5 | 3276
243 | Sh 47 (#4 @ 12" T&B; #5 edge bars w/ #3 stirrups @ 18"; 8" x #4 epoxy dowels @ 4') | 24 | Reinforcing steel Gr 60, generator pad (#4 @ 12" T&B EW, #5 edge bars, #3 stirrups, #4 dowels) | 720 | 10% | 792 | LB | 0.8 | 0.95 | 633.6 | 752.4 | 1386
APRON SLAB 4"
244 | Sh 47 (4" pad typical, 3 ft wide) | 24 | 4" concrete apron slab, 3'-0" wide around generator pad | 2.4 | 5% | 2.52 | CY | 260 | 220 | 655.2 | 554.4 | 1209.6
245 | Sh 47 (#4 bars @ 8" OCBW in 4" pad) | 24 | Reinforcing steel Gr 60, apron #4 @ 8" OC both ways | 444 | 10% | 488.4 | LB | 0.8 | 0.95 | 390.72 | 463.98 | 854.7
|  |  | Subtotal | [6 empty] | 3790.1184 | 3709.9788 | 7500.0972
|  |  | TOTAL AMOUNT, BASE BID (Section A) | [6 empty] | 803164.8032 | 1077435.5373 | 1880600.3405
|  |  | MOBILIZATION (10%) |  |  |  |  | 10% |  |  |  | 188060.034
|  |  | PROFIT (10%) |  |  |  |  | 10% |  |  |  | 188060.034
|  |  | OVERHEAD (20%) |  |  |  |  | 20% |  |  |  | 376120.0681
|  |  | INSURANCE (1%) |  |  |  |  | 1% |  |  |  | 18806.0034
|  |  | SUPERVISION (9%) |  |  |  |  | 9% |  |  |  | 169254.0306
|  |  | TOTAL BASE BID (excl. MEP, incl. markups) | [8 empty] | 2820900.5107
|  | ALT 1 | ALTERNATE 1: AWNING / CANOPY & FOUNDATION OVER EXISTING ELECTRICAL RACK AT WELL NO. 4 (Civil)
DEMOLITION & PROTECTION OF EXISTING
246 | Sh 7 Alt. Notes 10 | ALT 1 | Remove existing canopy roof & cap existing columns prior to new canopy | 1 | 0% | 1 | LS | 2800 | 600 | 2800 | 600 | 3400
247 | Sh 7 Alt. Note 8; Sh 7 (critical locate) | ALT 1 | Critical locate & protect existing facilities, lights & antenna during canopy work (electrical relocation excluded, MEP) | 1 | 0% | 1 | LS | 1500 | 300 | 1500 | 300 | 1800
FOUNDATIONS
248 | Sh 15 (Drilled Shaft Detail, 1'-6" dia x 10'-0", 6-#6 vert., #3 spiral @ 6") | ALT 1 | Drilled shaft foundations for canopy columns, 18" dia x 10'-0", 4,000 psi, 6-#6 verticals & #3 spiral hooping | 6 | 0% | 6 | EA | 850 | 650 | 5100 | 3900 | 9000
CANOPY STRUCTURE & ROOFING
249 | Sh 7 (8.5' x 24' canopy); Alt. Notes 1-6, 9 | ALT 1 | Pre-engineered HDG steel canopy (A572 Gr 50 W-flange beams, A500 Gr B tube, A36 plate), ASCE 7-22, 25 psf uplift, ±8' clear to match existing, engineered submittal | 204 | 0% | 204 | SF | 22 | 48 | 4488 | 9792 | 14280
250 | Sh 7 Alt. Note 7 | ALT 1 | 24 ga standing seam steel roof panels MPN120, 70% PVDF finish, w/ trim & closures | 204 | 10% | 224.4 | SF | 5.5 | 7.5 | 1234.2 | 1683 | 2917.2
|  |  | Subtotal | [6 empty] | 15122.2 | 16275 | 31397.2
|  | ALT 2 | ALTERNATE 2: ELECTRICAL EQUIPMENT SHELTER, FOUNDATION & RACK REMOVAL/REPLACEMENT AT WELL NO. 4 (Structural shelter only, electrical excluded)
DEMOLITION
251 | Sh 46 (Demolition, Remote Well No. 4 Electrical Equipment Rack) | ALT 2 | Demolition of existing electrical equipment rack & canopy; temporary support / power continuity of existing equipment | 1 | 0% | 1 | LS | 3500 | 1200 | 3500 | 1200 | 4700
FOUNDATION & SLAB
252 | Sh 46 (Shelter Front/End View) | ALT 2 | Shelter concrete slab 6" w/ #4 @ 16" EW & perimeter beam, concrete post shafts (5'-0" embed), ±6'-0" x 26'-0" | 5.5 | 5% | 5.775 | CY | 400 | 380 | 2310 | 2194.5 | 4504.5
STEEL FRAMING
253 | Sh 46 | ALT 2 | HSS 4"x4"x1/4" HDG posts (approx. 15'-0" long) | 6 | 0% | 6 | EA | 250 | 520 | 1500 | 3120 | 4620
254 | Sh 46 (C3x4.1 frame rails, C6x8.2, hat channels, 1/2" thru bolts) | ALT 2 | HDG C3x4.1 frame rails, C6x8.2 roof beams, hat channel spacers & connections | 1 | 0% | 1 | LS | 2800 | 3600 | 2800 | 3600 | 6400
ROOF & WALL PANELS
255 | Sh 46 (26 ga galv. R-panel roof & wall) | ALT 2 | 26 ga galvanized R-panel roof (3:12) & back/end walls w/ closure trim | 420 | 10% | 462 | SF | 2.75 | 2.4 | 1270.5 | 1108.8 | 2379.3
|  |  | Subtotal | [6 empty] | 11380.5 | 11223.3 | 22603.8
|  | ALT 4 | ALTERNATE 4: REMOVABLE WELL PROTECTION FENCING, WELL NO. 4 (Sh 7, 20)
FENCE LINE (FABRIC, REMOVABLE POSTS, FOOTINGS & SCREEN)
256 | Sh 7 (64 LF + 16 LF), Sh 20 (Remote Well No. 4 Site) | ALT 4 | 8'-0" high chain link well protection fence w/ braces, tension wire & rods | 80 | 0% | 80 | LF | 9.5 | 12.5 | 760 | 1000 | 1760
257 | Sh 20 (Removable Post Detail) | ALT 4 | 4" OD removable posts in HSS 4.500" x 0.188" sleeves, 18" dia x 4'-0" footings @ 8' max | 13 | 0% | 13 | EA | 185 | 245 | 2405 | 3185 | 5590
258 | Sh 20 & 21 | ALT 4 | PVC privacy mesh screen 90% blockage | 640 | 5% | 672 | SF | 0.55 | 0.85 | 369.6 | 571.2 | 940.8
GATE & PIPE OPENING
259 | Sh 20 | ALT 4 | Pedestrian gate 4'-0" w/ Type 71 latch | 1 | 0% | 1 | EA | 250 | 650 | 250 | 650 | 900
260 | Sh 20 (with opening) | ALT 4 | Fence panel with framed pipe opening | 1 | 0% | 1 | EA | 200 | 250 | 200 | 250 | 450
|  |  | Subtotal | [6 empty] | 3984.6 | 5656.2 | 9640.8
|  |  | TOTAL AMOUNT, ALTERNATE BID ITEMS (Section C) | [6 empty] | 30487.3 | 33154.5 | 63641.8
|  |  | MARKUPS ON ALTERNATES (same % as base bid) |  |  |  |  | 50% |  |  |  | 31820.9
|  |  | TOTAL ALTERNATE BID ITEMS (Section C incl. markups) | [8 empty] | 95462.7
NOTES:
Furnish & Installation
Quantities highlighted yellow are scaled, routed or calculated where plans give no dimension; verify before pricing. Other quantities are taken from plan dimensions, schedules, bid form or specifications. Quantity basis is shown in the Remarks column.
Quantities in column F are net; column G carries material waste/overage only.
MEP EXCLUDED (electrical, generator/gas, plumbing fixtures, HVAC) incl. Bid Form MEP allowances, see CLARIFICATIONS. Alternates (Section C) are priced separately.
See sheet "CLARIFICATIONS" for drawing / specification discrepancies used as the basis of this BOQ.

## CLARIFICATIONS
# | QUANTITY / SCOPE CLARIFICATIONS & DISCREPANCIES (for RFI / bid qualification)
1 | Addendum No. 1 governs: open hole is 8-3/4" (Spec 13200 §1.06 and Sheet 10 show 9-7/8"). 2nd pilot hole = 630 VF (1,890' to 2,520'). WP-242 deleted; WP-240 & 15100 added.
2 | Bid Form Item 3 = 380 LF chain link; drawings show 280 LF + 130 LF less 16' & 10' gates = 384 LF (Sheet 5). BOQ carries 384 LF.
3 | Bid Form Item 17 lists 802' of 16" and 1,088' of 10" casing; Sheet 10 additionally shows 26" x 0.375" surface casing 0' to 40' in 30" hole, carried as separate lines.
4 | Spec 13200 §1.06 design table appears transposed (casing bottom 2,520' / open hole bottom 1,890'); BOQ follows Sheet 10 profile and Addendum 1.
5 | Well pump foundation rebar: Sheet 11 shows #4 @ 18" EW; Spec 13200 §3.25 requires #5 @ 12" EW each face, priced per spec (more stringent).
6 | Sounder tube: Sheet 10 = 1" PVC E-line; Spec 13200 §2.17 = 1-1/4" Sch 40 PVC. Chemical insertion tubing (Bid Item 19) not detailed, RFI.
7 | Doors: Sheet 12 (Rev.) schedule = fiberglass door & frame; Sheet 3 Note 17 = galvanized steel; Sheet 15 = SS hollow metal frame. Schedule carried.
8 | Chlorine solution line: Sheet 5/12 = 3/4" PVC; Sheet 14 elevation = 1" chlorine chemical line in 2" PVC conduit.
9 | Masonry grout: Sheet 3 General Structural Note 12 = 2,500 psi fine grout; CMU Note 2 = 2,000 psi coarse grout, 2,500 psi carried.
10 | Generator pad and apron sized from Sheet 47 (enclosure 211" x 90"), adjust to final approved enclosure (Sheet 24 Note 11 requires +6" all sides).
11 | Grading/seeding areas scaled from Sheet 8 'extent of proposed grading' (no earthwork volumes provided), highlighted; verify against topo.
12 | No prevailing wage determination included in bid documents; verify Tex. Gov't Code Ch. 2258 requirement with City.
13 | Unit pricing columns (J, K) are left open for pricing; all extension, subtotal and markup formulas are live.
14 | MEP EXCLUDED per client instruction: electrical (Bid Item 23, Alt 3 & electrical portion of Alt 2), generator & natural gas (Bid Item 24, structural pad retained), emergency shower/eyewash & bladder tank (Bid Item 8), building HVAC/fans/heater, floor drain, transformer pad/bollards, and MEP allowances (electrical service $20,000, McCauley programming $15,000, gas service $5,000).
Documents reviewed: Plans (51 sheets, 7/29/2026), Project Manual incl. Technical Specs, Electrical Specs & Geotechnical Report (ARIAS), Addendum No. 1 (38 pp., 8/20/2026) incl. revised Bid Form, Spec 15100, WP-240 and revised Sheet 12.